## Sheet1
Form Section | Form Field | Manual imput | Calculated | Comments
1. Servicing Contractor Info | Technician Name | x
| Email | x
| Technician Mobile Number | x
| Company Name | x
| Street Address | x
| City | x
| State | x
| Zip Code | x
| Company Phone Number | x
| Submit This Info sheet To | x
2. Homeowner Info | Homeowner Name | x
| Street Address | x
| City | x
| State | x
| Zip Code | x
3. JSIS Type and Equipment Data | Select the JSIS type | x
| Select the system configuration | x
| Air Handler/Furnace Model # | x
| Air Handler/Furnace Serial # | x
| Air Handler/Furnace Location | x
| Air Handler/Furnace Air Flow Direction | x
| Problem Descrition - Sumary | x
| Problem Descrition - Corrctive Actions Taken | x
| Accesories Installed | x
4. Air Temperatures | Outdoor Air Temperature | x
| Indoor Dry Bulb Temperature | x
5. Refrigerant Data | Refrigerant Type | x
| Other Type of Refrigerant | x
| High Side - Gauge Pressure | x
| High Side - Physical Temperature | x
| High Side - Saturation Temperature | x | x | Table based on Refrigerant type and "High Side - Guage Pressure"
| High Side - Sub-cooling Value | x | x | = "High Side - Saturation Temperature" - "High Side - Physical Temperature"
| Low Side - Gauge Pressure | x
| Low Side - Physical Temperature | x
| Low Side - Saturation Temperature | x | x | Table based on Refrigerant type and "Low Side - Guage Pressure"
| Low Side - Superheat Value | x | x | = "Low Side - Physical Temperature" - "Low Side - Saturation Temperature"
6. Refrigerant Line Temperatures | Compressor Line Temperatures - Suction Line Temperature | x
| Compressor Line Temperatures - Discharge Line Temperature | x
| Outdoor Unit Coil Temperatures - Inlet Line Temperature | x
| Outdoor Unit Coil Temperatures - Discharge Line Temperature | x
| Filter Drier Temperatures - Inlet Line Temperature | x
| Filter Drier Temperatures - Discharge Line Temperature | x
| Indoor Unit Coil Temperatures - Inlet Line Temperature | x
| Indoor Unit Coil Temperatures - Discharge Line Temperature | x
7. Electrical Data | Voltage Phase | x
| Supply Voltage: Neutral-L1 | x
| Supply Voltage: Neutral-L2 | x
| Supply Voltage: Neutral-L3 | x
| Supply Voltage: L1-L2 | x | x
| Supply Voltage: L1-L2 | x | x
| Supply Voltage: L1-L2 | x | x
| Compressor Amps - L1 Terminal | x
| Compressor Amps - L2 Terminal | x
| Compressor Amps - L3 Terminal | x
| Compressor Amps - Common Winding | x
| Compressor Amps - Run Winding | x
| Compressor Amps - Start Winding | x
8. Airflow Data | Airflow Test Method | x
| Supply Side Static Pressure | x |  | Positive Number
| Return Side Static Pressure | x |  | Negative number (make negative if they enter a postivive)
| Total External Static Pressure | x | x | = "Supply Side Static Pressure" - "Return Side Static Pressure"
| (Static Pressure) Calculated CFM | x | x | (no formula for this - must be manual entry
| Measured Heating Element Voltage | x
| Measured Heating Element Amperage | x
| Supply Temperature | x
| Return Temperature | x
| Measured Temperature Rise | x | x | = "Supply Temperature" - "Return Temperature"
| Approximate Height Above Sea Level | x |  | Use a Table to give "SHC" Data
| (AHU Temp Rise) Calculated CFM |  |  | = (("Measured Heating Element Voltage" x "Measured Heating Element Amperage" x 3.414) / (("Supply Temperature" - "Return Temperature") x (SHC))
| Total Supply CFM | x
| Total Return CFM | x
| Flowhood Test Method | x
9. Additional Data | Liquid Line Size | x
| Vapor Line Size | x
| Total Length | x
| Vertical Separation | x